## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KTICHEN | 9500 | 8674 | 7600 | 8037 | 1900 | 637 | 20% | 7.344%
AC-2 | DINING A | 3150 | 3259 | 2520 | 2631 | 630 | 628 | 20% | 19.27%
AC-3 | DINING B | 5000 | 5314 | 4000 | 4277 | 1000 | 1037 | 20% | 19.51%
AC-4 | PLAY AREA | 2000 | 1916 | 1600 | 1541 | 400 | 375 | 20% | 19.57%
AC-5 | BOH/OFFICE | 1200 | 1250 | 960 | 988 | 240 | 262 | 20% | 20.96%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 2088
EF-2 | HOOD 2 | [10 empty] | 701 | 0
EF-3 | RESTROOM | [12 empty] | 500 | 565
EF-4 | HOOD 3 | [10 empty] | 390 | 391
TOTALS |  | 20850 | 20413 | 16680 | 17474 | 4170 | 2939 |  |  | 0 | 0 | 3003 | 2479 | 500 | 565
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 4170 | 2939 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | TRUE
TOTAL EXHAUST |  | 3503 | 3044 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 667 | -105 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
IN THIS CONDITION WE READ THE BUILDING PRESSURE TO BE APPROXIMETLEY NUETRAL. ONCE AC#1 ECONOMIZER IS FIXED AND EF#2, BUILDING PRESSURE IS EXPECTED TO BECOME POSOTIVE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390