## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3750 | 3596 | 3250 | 3122 | 500 | 474 | 13.33% | 13.18%
RTU-2 | DINING | 4400 | 4447 | 3400 | 3395 | 1000 | 1052 | 22.73% | 23.66%
MUA-1 | KITCHEN HD | [8 empty] | 1300 | 1286
EF-1 | KITCHEN HD | [10 empty] | 2550 | 2755
EF-2 | RESTROOM | [12 empty] | 150 | 147
TOTALS |  | 8150 | 8043 | 6650 | 6517 | 1500 | 1526 |  |  | 1300 | 1286 | 2550 | 2755 | 150 | 147
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2800 | 2812 |  | FRONT |  | -0.0067 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2700 | 2902 |  | SIDE |  | -0.0068 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | -90 |  | REAR |  | -0.0068 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0067667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0