## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4000 | 4178 | 3500 | 3663 | 500 | 515 | 12.5% | 12.33%
RTU-2 | DINING | 4325 | 4644 | 3325 | 3667 | 1000 | 977 | 23.12% | 21.04%
MUA-1 | KITCHEN HOOD | [8 empty] | 1300 | 1327
EF-1 | KITCHEN HOOD | [10 empty] | 2550 | 2513
EF-2 | RESTROOM | [12 empty] | 150 | 155
TOTALS |  | 8325 | 8822 | 6825 | 7330 | 1500 | 1492 |  |  | 1300 | 1327 | 2550 | 2513 | 150 | 155
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2819 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2700 | 2668 |  | SIDE |  | 0.003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 151 |  | REAR |  | 0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.003 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
BUILDNING PRESSURE IS ESTIMATED AND NOT MEASURED DUE TO ABORNORMAL READINGS AT SITE.THIS CAN BE ATTRIBUTED TO THE BUILDINGS ROOF NOT BEING SEALED, CEILING TILES NOT BEING INSTALLED, AND WINDY WEATHER CONDITIONS ON THE DAY OF TESTING.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250