## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 3806 | 4100 | 2880 | 900 | 926 | 18% | 24.33%
DOAS-1 | KITCHEN | 3300 | 3270 | 0 | 0 | 3300 | 3270 | 100% | 100%
KEF-1 | GRDDILE | [10 empty] | 2584 | 2527
KEF-2 | FRYER | [10 empty] | 775 | 797
KEF-3 | DISHES | [10 empty] | 525 | 533
EF-1 | RR | [12 empty] | 150 | 93
EF-2 | RR | [12 empty] | 75 | 56
TOTALS |  | 8300 | 7076 | 4100 | 2880 | 4200 | 4196 |  |  | 0 | 0 | 3884 | 3857 | 225 | 149
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4200 | 4196 |  | FRONT |  | 0.0011 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4109 | 4006 |  | SIDE |  | -0.0001 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 91 | 190 |  | REAR |  | 0.0017 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0009 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0