## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3570 | 2900 | 3029 | 500 | 541 | 14.71% | 15.15%
RTU-2 | DINING | 3000 | 3135 | 2000 | 2063 | 1000 | 1072 | 33.33% | 34.19%
MUA-1 | KITCHEN HOOD | [8 empty] | 1650 | 1677
EF-1 | KITCHEN HOOD | [10 empty] | 2800 | 2755
EF-2 | RESTROOM | [12 empty] | 75 | 72
TOTALS |  | 6400 | 6705 | 4900 | 5092 | 1500 | 1613 |  |  | 1650 | 1677 | 2800 | 2755 | 75 | 72
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3150 | 3290 |  | FRONT |  | 0.0065 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2875 | 2827 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 275 | 463 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0065 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 160X12 |  | 1650 |  | 2800 |  | -1150