## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-102-1 | DINING ROOM 2830 | 4350 | 4292 | 3750 | 3689 | 600 | 603 | 13.79% | 14.05%
RTU-1023 | KITCHEN | 2800 | 2550 | 1600 | 1307 | 1200 | 1243 | 42.86% | 48.75%
FCU-1 | OFFICE |  |  |  |  | 40 | 0
KEF-1 | HOOD 1 | [10 empty] | 1450 | 1541
EF-1 | RESTROOMS | [12 empty] | 150 | 148
EF-2 | TRASH ROOM | [12 empty] | 100 | 172
TOTALS |  | 7150 | 6842 | 5350 | 4996 | 1840 | 1846 |  |  | 0 | 0 | 1450 | 1541 | 150 | 148
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1840 | 1846 |  | FRONT |  | 0.002 | [8 empty] | TRUE | FALSE | FALSE | RTU 1 DESIGN FM = 2833
TOTAL EXHAUST |  | 1600 | 1689 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 240 | 157 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.003 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 1200 | 1243
TOTAL KITCHEN EXHAUST |  | 1450 | 1541
NET AIRFLOW |  | -250 | -298
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0