## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3040 | 3183 | 2275 | 2059 | 765 | 1124 | 25.16% | 35.31%
RTU-2 | DINING | 3040 | 3175 | 2275 | 2082 | 765 | 1093 | 25.16% | 34.43%
RTU-3 | DINING | 2160 | 2206 | 1620 | 2206 | 540 | 0 | 25% | 0%
RTU-4 | KITCHEN | 6650 | 6395 | 5300 | 5037 | 1350 | 1358 | 20.3% | 21.24%
MUA-1 | COOKLINE | [8 empty] | 4425 | 4362
KEF-1 | HOOD 1 | [10 empty] | 1665 | 1810
KEF-2 | HOOD 2 | [10 empty] | 1665 | 1797
KEF-3 | HOOD 3 | [10 empty] | 1665 | 1797
KEF-4 | HOOD 4 | [10 empty] | 600 | 641
DEF-1 | DISH HOD | [10 empty] | 900 | 891
TEF-1 | RESTROOMS | [12 empty] | 600 | 606
TOTALS |  | 14890 | 14959 | 11470 | 11384 | 3420 | 3575 |  |  | 4425 | 4362 | 6495 | 6936 | 600 | 606
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 7845 | 7937 |  | FRONT |  | 0.0137 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 7095 | 7542 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 750 | 395 |  | REAR |  | 0.0043 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.009 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
OA intake for RTU-1 and RTU-2 were increased to compensate missing OA from RTU-3
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0