## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 1600 | 1050 | 1280 | 1050 | 320 | 0 | 20% | 0%
RTU-2 | DINING | 2000 | 1842 | 1600 | 1467 | 400 | 375 | 20% | 20.36%
RTU-3 | KITCHEN | 3000 | 2783 | 2400 | 2233 | 600 | 550 | 20% | 19.76%
MUA-1 | HOODS 1 & 2 | [8 empty] | 2350 | 1268
EF-1 | HOODS 1 & 2 | [10 empty] | 3600 | 3535
EF-2 | RESTROOMS | [12 empty] | 150 | 0
TOTALS |  | 6600 | 5675 | 5280 | 4750 | 1320 | 925 |  |  | 2350 | 1268 | 3600 | 3535 | 150 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3670 | 2193 |  | FRONT |  | 0.0025 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3750 | 3535 |  | SIDE |  | NA |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | -80 | -1342 |  | REAR |  | 0.029 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.01575 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD1 | CAPTIVEAIRE |  | CAPTRATE SOLO/ 16X16/ 2016 |  |  |  | DD |  | 108" |  | 634 |  | 1714 |  | -1080
HD2 | CAPTIVEAIRE |  | CAPTRATE SOLO/ 16X16/ 2016 |  |  |  | DD |  | 108" |  | 634 |  | 1821 |  | -1187
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0