## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 9093 | 7000 | 7261 | 1750 | 1832 | 20% | 20.15%
AC-2 | SERVING | 5250 | 5394 | 4100 | 4196 | 1150 | 1198 | 21.9% | 22.21%
AC-3 | DINING | 5250 | 5252 | 4000 | 4108 | 1250 | 1144 | 23.81% | 21.78%
AC-4 | TEAM MEMBER ROOM/OFFICE | 2100 | 2058 | 1600 | 1559 | 500 | 499 | 23.81% | 24.25%
AC-5 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1854
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1413
EF-3 | RESTROOM | [12 empty] | 375 | 389
TOTALS |  | 21350 | 21797 | 16700 | 17124 | 4650 | 4673 |  |  | 0 | 0 | 3314 | 3267 | 375 | 389
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4673 |  | FRONT |  | 0.0208 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3689 | 3656 |  | SIDE |  | 0.0173 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 961 | 1017 |  | REAR |  | 0.0151 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0177 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390