## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | CORE | 3400 | 3360 | 2900 | 2833 | 500 | 527 | 14.71% | 15.68%
RTU-2 | DELI | 5000 | 4996 | 4500 | 4473 | 500 | 523 | 10% | 10.47%
RTU-3 | RETAIL | 3000 | 2962 | 2725 | 2694 | 275 | 268 | 9.167% | 9.048%
EF-1 | RESTROOMS | [12 empty] | 325 | 332
EF-2 | BOH | [12 empty] | 450 | 444
TOTALS |  | 11400 | 11318 | 10125 | 10000 | 1275 | 1318 |  |  | 0 | 0 | 0 | 0 | 775 | 776
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1275 | 1318 |  | FRONT |  | 0.0079 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 775 | 776 |  | SIDE |  | 0.0066 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 500 | 542 |  | REAR |  | 0.0146 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0097 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0