## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | Dinning | 4000 | 3787 | 3280 | 3069 | 720 | 718 | 18% | 18.96%
RTU-2 | Kitchen | 4000 | 3956 | 3280 | 3227 | 720 | 729 | 18% | 18.43%
MUA-1 | Hood 1 & 2 | [8 empty] | 1900 | 1860
KEF-1 | Hood 1 | [10 empty] | 1800 | 1846
KEF-2 | Hood 2 | [10 empty] | 775 | 763
KEF-3 | Hood 3 | [10 empty] | 525 | 582
EF-1 | Restroom | [12 empty] | 75 | 61
EF-2 | Restroom | [12 empty] | 150 | 18
EF-3 | Restroom | [12 empty] | 75 | 59
TOTALS |  | 8000 | 7743 | 6560 | 6296 | 1440 | 1447 |  |  | 1900 | 1860 | 3100 | 3191 | 300 | 138
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3340 | 3307 |  | FRONT |  | -0.011 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3400 | 3329 |  | SIDE |  | 0.007 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -60 | -22 |  | REAR |  | -0.015 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0063333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES: