## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3000 | 2867 | 1950 | 1796 | 1050 | 1071 | 35% | 37.36%
RTU-2 | DINING | 3000 | 3070 | 1950 | 2009 | 1050 | 1061 | 35% | 34.56%
EF-1 | KITCHEN HOOD | [10 empty] | 1900 | 1905
EF-2 | RESTROOM | [12 empty] | 150 | 153
TOTALS |  | 6000 | 5937 | 3900 | 3805 | 2100 | 2132 |  |  | 0 | 0 | 1900 | 1905 | 150 | 153
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2100 | 2132 |  | FRONT |  | 0.0013 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2050 | 2058 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 74 |  | REAR |  | 0.0008 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00105 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 7 16X16 | [7 empty] | 0 |  | 1900 |  | -1900