Project Summary

Preface

The summary below provides a quick understanding of how well your HVAC systems balanced in respect to the design criteria. The summary concludes with a quick understanding of your building environment and possible suggestions for each of your systems after testing has been performed. Our focus is to work with the trades to remedy any issues or deficiencies during the actual field balancing and not after the balancing has occurred. Our focus is to achieve a positive environment and outcome. The level of success is determined by the availability of the trades, possible parts needed, or time constraints. Also, enclosed are pictures of building assets and items listed below that will provide your team with more insight.

Facility Identification and TAB Requirements

The mechanical equipment to be tested, adjusted, and balanced includes: All Fan-Coil Units (FCU), All Exhaust Fans (EF), All Dedicated Outdoor Air Systems (DOAS), and all associated air devices.

FCU’s

Each of the FCU’s were measured at their terminal devices utilizing a flow hood or with a velgrid and K factor.  The sum of these readings is equal to the total flow for that particular unit.  The total flow of each FCU was then adjusted to within tolerance of the specified design. Each terminal diffuser was balanced to  within tolerance of the engineer’s design volume utilizing the provided hand damper located at the takeoff of the main & branch trunk line(s). Any equipment that fell outside of this tolerance is noted throughout the report.

DOAS

The DOAS unit supplies outside air to the individual fan coil units. The total airflow for this unit was measured via traverse and then the individual branches were balanced where possible. Not all branches to the individual fan coils could be measured due to accessibility. The total flow for the unit was successfully balanced.

General Exhaust Fans

The general exhaust fans were measured by reading each air device with a flow hood. The total airflow for each fan is equivalent to the sum of these readings. Fan speed was then adjusted so that the airflow was within tolerance of design. Each terminal device was balanced to within tolerance of the design volume using the installed volume dampers. Any equipment that fell outside of this tolerance is noted throughout the report.