## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3000 | 3056 | 2500 | 2514 | 500 | 542 | 16.67% | 17.74%
RTU-2 | DINING | 3400 | 3662 | 2400 | 2631 | 1000 | 1031 | 29.41% | 28.15%
RTU-3 | STORAGE ROOM | 960 | 1040 | 900 | 977 | 60 | 63 | 6.25% | 6.058%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1911
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3175
EF-2 | RESTROOM | [12 empty] | 150 | 156
TOTALS |  | 7360 | 7758 | 5800 | 6122 | 1560 | 1636 |  |  | 1950 | 1911 | 3200 | 3175 | 150 | 156
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3510 | 3547 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3350 | 3331 |  | SIDE |  | 0.0102 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 160 | 216 |  | REAR |  | 0.0082 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0071333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250