## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6125 | 5578 | 5175 | 4183 | 950 | 1395 | 15.51% | 25.01%
RTU-2 | BAR DINING | 6125 | 4582 | 5175 | 3632 | 950 | 950 | 15.51% | 20.73%
RTU-3 | KITCHEN | 6000 | 4556 | 5250 | 3528 | 750 | 1028 | 12.5% | 22.56%
MUA-1 | HOOD 1, 2, 3 | [8 empty] | 5088 | 5212
EF-1 | HOOD 1 | [10 empty] | 1800 | 2107
EF-2 | HOOD 2 | [10 empty] | 3160 | 2883
EF-3 | HOOD 3 | [10 empty] | 1400 | 1251
EF-4 | DISH HOOD 4 | [10 empty] | 900 | 961
EF-5 | RESTROOMS | [12 empty] | 600 | 501
TOTALS |  | 18250 | 14716 | 15600 | 11343 | 2650 | 3373 |  |  | 5088 | 5212 | 7260 | 7202 | 600 | 501
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 7738 | 8585 |  | FRONT |  | 0.03 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 7860 | 7703 |  | SIDE |  | 0.04 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -122 | 882 |  | REAR |  | n/a | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.035 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE | [5 empty] | PSP |  |  |  | 1440 |  | 1800 |  | -360
HD | CAPTIVE-AIRE | [5 empty] | PSP |  |  |  | 2528 |  | 3160 |  | -632
HD | CAPTIVE-AIRE | [5 empty] | PSP |  |  |  | 1120 |  | 1400 |  | -280
HD | CAPTIVE-AIRE | [5 empty] | NA | [5 empty] | 900 |  | -900

## Sheet1
226 | 320.92
220 | 312.4
211 | 299.62 |  | rtu 1 | 4702 | 1345
206 | 292.52 |  | rtu 2 | 4582 | 1506
| 0 |  | rtu 3 | 4556 | 1154
448 | 636.16
| 0 |  | hood 1 |  | 2107 | 1620 | 487
| 0 |  | hood 2 |  | 2883 | 2687 | 196
| 0 |  | hood 3 |  | 1251 | 905 | 346
[6 empty] | 5212 |  | 70
70
72
| 4702 | 5578.1906
| 703 | 834