## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BOH | 1050 | 1057 | 590 | 452 | 460 | 605 | 43.81% | 57.24%
RTU-2 | STOCKROOM | 1540 | 1624 | 970 | 1624 | 570 | 0 | 37.01% | 0%
RTU-3 | SALES | 1800 | 1716 | 1110 | 1716 | 690 | 0 | 38.33% | 0%
RTU-4 | SALES | 1800 | 1689 | 1110 | 1010 | 690 | 679 | 38.33% | 40.2%
RTU-5 | SALES | 1800 | 1921 | 1110 | 1220 | 690 | 701 | 38.33% | 36.49%
RTU-6 | SALES | 1800 | 1959 | 1110 | 1249 | 690 | 710 | 38.33% | 36.24%
RTU-7 | SALES | 2000 | 2122 | 2000 | 2122 | 0 | 0 | 0% | 0%
EF-1 | RESTROOM | [12 empty] | 250 | 228
EF-2 | IT CLOSET | [12 empty] | 1000 | 983
TOTALS |  | 11790 | 12088 | 8000 | 9393 | 3790 | 2695 |  |  | 0 | 0 | 0 | 0 | 1250 | 1211
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3790 | 2695 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1250 | 1211 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2540 | 1484 |  | REAR |  | 0.0101 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00755 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0