## 2EP-2925
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
TRANE |  |  | RTU-1 | KITCHEN | 500 |  | 0 |  |  | 890 / 790 | 2 | 460 | 3 | 6 | 4 | 3 | 1.3333 | 1 | -25%
TRANE |  |  | RTU-2 | DINING | 1000 |  | 1000 |  |  |  | 1 |  |  | 4 | 3 | 2 | 0.75 | 0.5 | -33.33%
CAPTIVE-AIRE |  |  | MUA-1 | HOOD 1 | 1775 |  | 1500 |  |  |  | 1 |  |  | 4 | 3 | 2 | 0.75 | 0.5 | -33.33%
CAPTIVE-AIRE |  |  | EF-1 | HOOD 1 | 2925 | 0 | 2200 |  |  |  | 1 |  |  | 4 | 3 | 2 | 0.75 | 0.5 | -33.33%
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150 | [10 empty] | #DIV/0!
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3275 | 0 | 2500 | 0 |  | FRONT DOOR | 2.5833 | 0 | INITIAL
|  |  | TOTAL EXHAUST |  | 3075 | 150 | 2350 | 150 |  | BACK DOOR | 1.5 | 0 | FINAL
|  |  | NET AIRFLOW |  | 200 | -150 | 150 | -150 |  | AVERAGE | -41.94% | 0 | NET CHANGE

## 2EP-3200
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
YORK | ZJ102N18R2B5EAA2A2 | N2D1930910 | RTU-1 | KITCHEN | 500 | 648 | 0 | 0 | 1766 | 1019 | 3 | 208 | 3 | 8.3 | 4.25 | 4.25 | 1.5361 | 1.5361 | 0%
YORK | ZJ102N18R2B5EAA2A2 | N2C1810777 | RTU-2 | DINING | 1000 | 611 | 1000 | 1063 | 1058 | 1760 | 3 | 208 | 3 | 8.3 | 4.14 | 4.14 | 1.4964 | 1.4964 | 0%
CAPTIVE-AIRE | A1-D-250-G10 | 4821838 | MUA-1 | HOOD 1 | 1950 | 1997 | 1875 | 1921 | 1755 / 1763 | 1217 / 1174 | 2 | 230 | 3 | 5.38 | 4.35 | 3.31 | 1.6171 | 1.2305 | -23.91%
CAPTIVE-AIRE | DU85HFA | 4821838 | EF-1 | HOOD 1 | 3200 | 1425 | 2650 | 1425 |  | 1278 | 0.75 | 115 | 1 | 8.9 | 6.9 | 6.9 | 0.58146 | 0.58146 | 0%
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3450 | 3256 | 2875 | 2984 | 0.021 | FRONT DOOR | 4.2311 | 3256 | INITIAL
|  |  | TOTAL EXHAUST |  | 3350 | 1575 | 2800 | 1575 | 0.022 | BACK DOOR | 3.8445 | 2984 | FINAL
|  |  | NET AIRFLOW |  | 100 | 1681 | 75 | 1409 | 0.021 | AVERAGE | -9.138% | 272 | NET CHANGE