## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3008 | 2900 | 2501 | 500 | 507 | 14.71% | 16.86%
RTU-2 | DINING | 3400 | 3446 | 2400 | 2406 | 1000 | 1040 | 29.41% | 30.18%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1817
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3321
EF-2 | RESTROOM | [12 empty] | 150 | 147
TOTALS |  | 6800 | 6454 | 5300 | 4907 | 1500 | 1547 |  |  | 1950 | 1817 | 3200 | 3321 | 150 | 147
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3450 | 3364 |  | FRONT |  | -0.0043 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3350 | 3468 |  | SIDE |  | 0.0058 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | -104 |  | REAR |  | -0.0127 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0037333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250