## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | RETAIL | 3400 | 3535 | 2875 | 3006 | 525 | 529 | 15.44% | 14.96%
RTU-2 | FOOD SERVICE | 4000 | 3950 | 3325 | 3323 | 675 | 627 | 16.88% | 15.87%
RTU-3 | RETAIL | 2000 | 1959 | 1700 | 1646 | 300 | 313 | 15% | 15.98%
EF-1 | RESTROOMS | [12 empty] | 300 | 303
EF-2 | BACKROOM | [12 empty] | 900 | 868
TOTALS |  | 9400 | 9444 | 7900 | 7975 | 1500 | 1469 |  |  | 0 | 0 | 0 | 0 | 1200 | 1171
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1500 | 1469 |  | FRONT |  | 0 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 1200 | 1171 |  | SIDE |  | -0.005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 300 | 298 |  | REAR |  | -0.012 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0056667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0