## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | WAITING/EXAM | 2673 | 3287 | 2273 | 2791 | 400 | 496 | 14.96% | 15.09%
FURNACE-1 | EXAM/STORAGE | 800 | 835 | 680 | 835 | 120 | 0 | 15% | 0%
EF-1 | RESTROOM | [12 empty] | 110 | 50
EF-2 | ADA RR | [12 empty] | 110 | 55
EF-3 | JANITOR | [12 empty] | 110 | 54
EF-3 | RESTROOM | [12 empty] | 110 | 53
TOTALS |  | 3473 | 4122 | 2953 | 3626 | 520 | 496 |  |  | 0 | 0 | 0 | 0 | 440 | 212
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 520 | 496 |  | FRONT |  | 0.0059 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 440 | 212 |  | SIDE |  | 0.0045 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 80 | 284 |  | REAR |  | 0.0062 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0059 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0