## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS-1 | KITCHEN | 4300 | 4460 | 0 | 0 | 4300 | 4460 | 100% | 100%
RTU-1 | DINING/BAR | 3700 | 3762 | 1900 | 1899 | 1800 | 1863 | 48.65% | 49.52%
RTU-2 | DINING | 2500 | 2337 | 700 | 501 | 1800 | 1836 | 72% | 78.56%
MUA-1 | COOKLINE | [8 empty] | 3800 | 3977
EF-1 | HOOD | [10 empty] | 2300 | 2446
EF-2 | HOOD | [10 empty] | 2300 | 2263
EF-3 | HOOD | [10 empty] | 3200 | 2920
EF-4 | HOOD | [10 empty] | 2200 | 2196
EF-5 | DISH HOOD | [12 empty] | 800 | 843
TEF-1 | RESTROOMS | [12 empty] | 400 | 396
TOTALS |  | 10500 | 10559 | 2600 | 2400 | 7900 | 8159 |  |  | 3800 | 3977 | 10000 | 9825 | 1200 | 1239
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 11700 | 12136 |  | FRONT
TOTAL EXHAUST |  | 11200 | 11064 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 500 | 1072 |  | REAR
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0 | TRUE | FALSE | FALSE
HD | [14 empty] | 0
HD | [14 empty] | 0 | #DIV/0! | #DIV/0! | FALSE
HD | [14 empty] | 0
#DIV/0!