## 2EP-2925
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
YORK | ZJ102N18D2B5HAA2A2 | N1K9282492 | RTU-1 | KITCHEN | 500 | 643 | 0 | 0 | 1725 | 1065 | 3 | 204.9 | 3 | 9.4 | 9.11 | 9.11 | 2.9074 | 2.9074 | 0%
YORK | ZJ090N18D2B5HAA2A2 | N1F9004626 | RTU-2 | DINING | 1000 | 1332 | 1000 | 990 | 1729 | 1054 | 3 | 205.5 | 3 | 9.4 | 9.01 | 9.01 | 2.8755 | 2.8755 | 0%
CAPTIVE-AIRE | A1-D.250-G10 | 3869322 | MUA-1 | HOOD 1 | 1775 | 2241 | 1500 | 1357 | 1760 / 1785 | 1115 / 784.2 | 2 | 209.3 | 3 | 5.38 | 4.01 | 2.42 | 1.4907 | 0.89963 | -39.65%
CAPTIVE-AIRE | NCA24HPFA | 3869322 | EF-1 | HOOD 1 | 2925 | 3029 | 2200 | 2332 | 1775 / 1787 | 801 / 692 | 2 | 208.13 | 3 | 5.9 | 3.11 | 2.63 | 1.0542 | 0.89153 | -15.43%
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150 | [10 empty] | #DIV/0!
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3275 | 4216 | 2500 | 2347 | 0.008 | FRONT DOOR | 7.3279 | 4216 | INITIAL
|  |  | TOTAL EXHAUST |  | 3075 | 3179 | 2350 | 2482 | -0.008 | BACK DOOR | 6.5741 | 2347 | FINAL
|  |  | NET AIRFLOW |  | 200 | 1037 | 150 | -135 | 0 | AVERAGE | -10.29% | 1869 | NET CHANGE

## 2EP-3200
AIR BALANCE SCHEDULE
UNIT TAG |  |  |  | AREA | INITIAL |  | FINAL |  | RPM CHANGE |  | POWER
MFG | MODEL | S/N | UNIT | SERVED | DESIGN | INITIAL | GOAL | FINAL | MOTOR RPM | FAN RPM | HP | RLV | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % change
TRANE |  |  | RTU-1 | KITCHEN | 500 |  | 0 |  |  | 890 / 790 | [6 empty] | #DIV/0! | #DIV/0! | #DIV/0!
TRANE |  |  | RTU-2 | DINING | 1000 |  | 1000 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
CAPTIVE-AIRE |  |  | MUA-1 | HOOD 1 | 1950 |  | 1875 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
CAPTIVE-AIRE |  |  | EF-1 | HOOD 1 | 3200 | 0 | 2650 | [9 empty] | #DIV/0! | #DIV/0! | #DIV/0!
NL - NOT TESTED |  |  | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL | FINAL B.P. |  | DELTA PWR | Delta Load
|  |  | TOTAL OA |  | 3450 | 0 | 2875 | 0 |  | FRONT DOOR | #DIV/0! | 0 | INITIAL
|  |  | TOTAL EXHAUST |  | 3350 | 150 | 2800 | 150 |  | BACK DOOR | #DIV/0! | 0 | FINAL
|  |  | NET AIRFLOW |  | 100 | -150 | 75 | -150 |  | AVERAGE | #DIV/0! | 0 | NET CHANGE