## Report Sheet
STORE #: | 3663 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | CANTON,OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 2 END PANEL - 156" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-24 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | MOHAMMED OUARD | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ090N12R2B5EAA2A2 | N2E0812506 | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1738 | 1738 | 907 | 907 | 1.5 | 215 | 215 | 3 | 2.8 | 5.4 | 5.4 | 1.9408 | 1.9408 | 0%
YORK | ZJ090N12R2B5EAA2A2 | N2E0812271 | RTU-2 | DINING | 1000 | 0 | 1000 | 983 |  | 1747 | 1747 | 1108 | 1108 | 3 | 214 | 214 | 3 | 8.3 | 8.15 | 8.1 | 2.9155 | 2.8976 | -0.6135%
CAPTIVE AIRE | A1-D.250-15D | 4249126 | MUA-1 | HOOD 1 | 1775 | 2268 | 1500 | 1540 | No | 2117 | 1479 | 2117 | 1479 | 2 | 128 | 85 | 3 | 5.48 | 4.7 | 3.6 | 1.0057 | 0.51152 | -49.14%
CAPTIVE AIRE | CASRE18DD | 4249126 | EF-1 | HOOD 1 | 2925 | 1735 | 2200 | 1735 | No | 1566 | 1566 | 1566 | 1566 | 2 | 110 | 110 | 3 | 5.38 | 4.3 | 4.3 | 0.79068 | 0.79068 | 0%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3275 | 2268 | 2500 | 2523 |  | FRONT DOOR |  | 0.0025 |  |  | INITIAL | 6.6526 | 2268
|  |  | TOTAL EXHAUST |  | 3075 | 1885 | 2350 | 1885 |  | BACK DOOR |  | 0.0151 |  |  | FINAL | 6.1406 | 4258
|  |  | NET AIRFLOW |  | 200 | 383 | 150 | 638 |  | AVERAGE |  | 0.0088 |  |  | ∆ | 0.51202 | -1990
Issue List
Unit # | Description
Select from drop down list
Unable to set fan vfd to a higher frequency MODBUS FAULT .CORRECT FAN ROTATION.FILTERS LOOK CLEAN .LOW FPM ON RIGHT SIDE.

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.