## Report Sheet
STORE #: | 3663 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | CANTON,OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 2 END PANEL - 156" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-05-24 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | MOHAMMED OUARD | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ090N12R2B5EAA2A2 | N2E0812506 | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1738 | 1738 | 907 | 907 | 1.5 | 215 | 215 | 3 | 2.8 | 5.4 | 5.4 | 1.9408 | 1.9408 | 0%
YORK | ZJ090N12R2B5EAA2A2 | N2E0812271 | RTU-2 | DINING | 1000 | 0 | 1000 | 983 |  | 1747 | 1747 | 1108 | 1108 | 3 | 214 | 214 | 3 | 8.3 | 8.15 | 8.1 | 2.9155 | 2.8976 | -0.6135%
CAPTIVE AIRE | A1-D.250-15D | 4249126 | MUA-1 | HOOD 1 | 1775 | 2268 | 1500 | 1540 | No | 2117 | 1479 | 2117 | 1479 | 2 | 128 | 85 | 3 | 5.48 | 4.7 | 3.6 | 1.0057 | 0.51152 | -49.14%
CAPTIVE AIRE | CASRE18DD | 4249126 | EF-1 | HOOD 1 | 2925 | 1735 | 2200 | 1735 | No | 1566 | 1566 | 1566 | 1566 | 2 | 110 | 110 | 3 | 5.38 | 4.3 | 4.3 | 0.79068 | 0.79068 | 0%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3275 | 2268 | 2500 | 2523 |  | FRONT DOOR |  | 0.0025 |  |  | INITIAL | 6.6526 | 2268
|  |  | TOTAL EXHAUST |  | 3075 | 1885 | 2350 | 1885 |  | BACK DOOR |  | 0.0151 |  |  | FINAL | 6.1406 | 4258
|  |  | NET AIRFLOW |  | 200 | 383 | 150 | 638 |  | AVERAGE |  | 0.0088 |  |  | ∆ | 0.51202 | -1990
Issue List
Unit # | Description
Select from drop down list
Exhaust airflow initially found below target.It appears the filters may be dirty and restricting airflow.Recommend deep cleaning or replacing before any airflow adjustments are made.

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not running / MUA is not running. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.