## SUMMARY (2)
AIR BALANCE SCHEDULE
|  |  | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT |  |  | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
WSHP-1 | 20 TONS | UPPER DINING | - | 5987 | #VALUE! | 5987 |  | 0 | #VALUE! | 0%
WSHP-2 | 20 TONS | BAR | - | 6673 | #VALUE! | 6673 |  | 0 | #VALUE! | 0%
HP-3 | 3 TONS | 2ND FLOOR PRIVATE DINING | - | 1156 | #VALUE! | 1156 |  | 0 | #VALUE! | 0%
HP-4 | 5 TONS | FRONT KITCHEN | - | 2256 | #VALUE! | 2256 |  | 0 | #VALUE! | 0%
HP-5 | 3 TONS | WINE | - | 1239 | #VALUE! | 1239 |  | 0 | #VALUE! | 0%
HP-6 | 3 TONS | SOUTH DINING | - | 1132 | #VALUE! | 1132 |  | 0 | #VALUE! | 0%
HP-7 | 3 TONS | PRIVATE DINING |  | 1256 | 0 | 1256 |  | 0 | #DIV/0! | 0%
HP-8 | 5 TONS | LOBBY / RR |  | 2226 | 0 | 2226 |  | 0 | #DIV/0! | 0%
HP-9 | 5 TONS | REAR KITCHEN |  | 1204 |  | 1204 |  | 0 |  | 0%
HP-10 | 3 TONS | SOUTH DINING HOST WALL |  | 1323 |  | 1323 |  | 0 |  | 0%
RTU-1 |  | STAIRWELL |  | 1106 |  | 1106 |  | 0 |  | 0%
RTU-2 | 5 TONS | POOL SOUTH |  | 2208 |  | 2208 |  | 0 |  | 0%
RTU-3 | 5 TONS | POOL NORTH | - | 2172 | #VALUE! | 2172 |  | 0 | #VALUE! | 0%
KEF-1 |  | HOOD-1 AND HOOD 2 | [11 empty] | 7163
KEF-2 |  | DISH HD-3 | [11 empty] | 1008
MAU |  | HOOD-1 AND HOOD 2 | [9 empty] | 9469
TOTALS |  |  | 0 | 29938 | #VALUE! | 29938 | 0 | 0 |  |  | 0 | 9469 | 0 | 8171 | 0 | 0
NET BUILDING AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  |  | 0 | 9469 |  | FRONT |  | 0.006 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  |  | 0 | 8171 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  |  | 0 | 1298 |  | REAR | [10 empty] | TRUE
[6 empty] | AVERAGE |  | 0.006 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT |  |  |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0
HD | [15 empty] | 0