## Report Sheet
STORE #: | 4117 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | WYLIE, TX | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-07-25 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
TRANE | GBC120A3ELA3YX9 | 224910041MX | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1758 | 1758 | 912 | 912 | 3 | 205.7 | 205.7 | 3 | 8.8 | 6.4 | 6.4 | 2.2007 | 2.2007 | 0%
TRANE | 48HCED11B2M5-6W4J0 | 0222P94547 | RTU-2 | DINING | 1000 | 0 | 1000 | 960 |  | 1767 | 1767 | 991 | 991 | 3 | 205.2 | 205.2 | 3 | 9.2 | 7.3 | 7.3 | 2.504 | 2.504 | 0%
CAPTIVE AIRE | A1-D.250-15D | 5023377 | MUA-1 | HOOD 1 | 1950 | 1751 | 1700 | 1751 | No | 1812 | 1812 | 1812 | 1812 | NA | 209 | 209 | 3 | 5.48 | 3.8 | 3.8 | 1.3276 | 1.3276 | 0%
CAPTIVE AIRE | DU240HFA | 5023377 | EF-1 | HOOD 1 | 3200 | 3078 | 2450 | 2284 | No | 840 | 644 | 840 | 644 | 3 | 208.9 | 211 | 3 | 9.2 | 6.3 | 4.6 | 2.2 | 1.6225 | -26.25%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 1751 | 2700 | 2711 |  | FRONT DOOR |  | 0.003 |  |  | INITIAL | 8.2323 | 1751
|  |  | TOTAL EXHAUST |  | 3350 | 3228 | 2600 | 2434 |  | BACK DOOR |  | -0.004 |  |  | FINAL | 7.6548 | 2711
|  |  | NET AIRFLOW |  | 100 | -1477 | 100 | 277 |  | AVERAGE |  | -0.0005 |  |  | ∆ | -0.5775 | 960
Issue List
Unit # | Description
Select from drop down list
Additional Notes:

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.