## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8100 | 7621 | 6100 | 5810 | 2000 | 1811 | 24.69% | 23.76%
AC-2 | SIDE DINING | 2830 | 2947 | 2050 | 2142 | 780 | 805 | 27.56% | 27.32%
AC-3 | MAIN DINING | 4000 | 3826 | 2970 | 2761 | 1030 | 1065 | 25.75% | 27.84%
AC-4 | MAIN DINING | 2765 | 2780 | 2135 | 2107 | 630 | 673 | 22.78% | 24.21%
AC-5 | PLAY AREA | 1800 | 1861 | 1500 | 1533 | 300 | 328 | 16.67% | 17.62%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1769
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1443
EF-3 | RESTROOM | [12 empty] | 400 | 407
TOTALS |  | 19495 | 19035 | 14755 | 14353 | 4740 | 4682 |  |  | 0 | 0 | 3315 | 3212 | 400 | 407
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4740 | 4682 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3715 | 3619 |  | SIDE |  | 0.007 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1025 | 1063 |  | REAR |  | 0.001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0043333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390