## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 8548 | 7250 | 7056 | 1500 | 1492 | 17.14% | 17.45%
AC-2 | RR. VEST | 1790 | 1736 | 1340 | 1237 | 450 | 499 | 25.14% | 28.74%
AC-3 | DRIVE THRU | 3000 | 3286 | 2350 | 2591 | 650 | 695 | 21.67% | 21.15%
AC-4 | S. DINING A | 4000 | 3482 | 3100 | 2586 | 900 | 896 | 22.5% | 25.73%
AC-5 | PLAY AREA | 1750 | 1859 | 1350 | 1429 | 400 | 430 | 22.86% | 23.13%
AC-6 | MULTI-PURPOSE | 1100 | 1090 | 850 | 1090 | 250 | 0 | 22.73% | 0%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1868
EF-2 | HOOD 2 | [10 empty] | 701 | 681
EF-3 | RESTROOM | [12 empty] | 300 | 315
EF-4 | HOOD 3 | [10 empty] | 701 | 732
TOTALS |  | 20390 | 20001 | 16240 | 15989 | 4150 | 4012 |  |  | 0 | 0 | 3314 | 3281 | 300 | 315
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4150 | 4012 |  | FRONT |  | 0.003 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3614 | 3596 |  | SIDE |  | 0.004 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 536 | 416 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0036667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390