## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4400 | 4078 | 3250 | 2856 | 1150 | 1222 | 26.14% | 29.97%
RTU-2 | DINING | 4400 | 4522 | 3400 | 3524 | 1000 | 998 | 22.73% | 22.07%
EF-1 | KITCHEN HOOD | [10 empty] | 1900 | 1882
EF-2 | RESTROOM | [12 empty] | 150 | 149
TOTALS |  | 8800 | 8600 | 6650 | 6380 | 2150 | 2220 |  |  | 0 | 0 | 1900 | 1882 | 150 | 149
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2150 | 2220 |  | FRONT |  | 0.0054 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2050 | 2031 |  | SIDE |  | 0.0071 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 189 |  | REAR |  | 0.0039 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0054667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 7 16X16 | [7 empty] | 0 |  | 1900 |  | -1900