## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9152 | 8020 | 7752 | 1480 | 1400 | 15.58% | 15.3%
AC-2 | SERVING. DRIVE THRU | 5250 | 4339 | 3975 | 3089 | 1275 | 1250 | 24.29% | 28.81%
AC-3 | DINING | 6000 | 5745 | 3975 | 3770 | 2025 | 1975 | 33.75% | 34.38%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1948
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1389
EF-3 | RESTROOM | [12 empty] | 300 | 309
TOTALS |  | 20750 | 19236 | 15970 | 14611 | 4780 | 4625 |  |  | 0 | 0 | 3314 | 3337 | 300 | 309
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4780 | 4625 |  | FRONT |  | 0.0217'' | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3614 | 3646 |  | SIDE |  | 0.0238'' |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1166 | 979 |  | REAR |  | 0.02 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.02 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390