## Sheet1
REGION FILL OUT
Building name | Silver Spring Metro Center 1
AHU number | 1&2 | 3&4 | 5&6 | 7&8 | 9&10 | 11&12 | 13&14 | 15&16 | 17&18 | 19&20 | 21
Current BAS | Silver Spring Metro Center 1 1&2: Niagara 3.8.111
Current BAS contractor (technician) | Silver Spring Metro Center 1 1&2: Pritchett Controls
O&M Name and Number | Silver Spring Metro Center 1 1&2: Heritage Contracting - 47PM0721D0004
Areas / floors serviced | G100 & G1 Hall/Locker Rms | 1st Floor | 2nd Floor | 3rd Floor | 4th Floor | 5th Floor | 6th Floor | 7th Floor | 8th Floor | 9th Floor | G1-101
space type(s) served | Silver Spring Metro Center 1 1&2: Office and Halls; Silver Spring Metro Center 1 3&4: Lobby, Offices, Conf Rm; Silver Spring Metro Center 1 5&6: Office
Standard and New Extended Operating Hours | bar: Silver Spring Metro Center 1 1&2
>Standard Start | 6am | 6am | 6am | 6am | 6am | 6am | 6am | 6am | 6am | 6am | 6am
>Standard End | 6pm | 6pm | 6pm | 6pm | 6pm | 6pm | 6pm | 6pm | 6pm | 6pm | 6pm
>New Start
>New End
Design OA Minimum (from existing drawings) | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317
Design OA Maximum (from existing drawings) | 2000 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400
ASHRAE MIN CFM of OA (calculated) | 365.14 | 683.64 | 796.2 | 1547 | 1372 | 1592 | 1422 | 1432 | 1377 | 1587 | 0 | 0 | 0
Sq ft of serviced area - 126,814 | 4419 | 9394 | 9270 | 15450 | 15450 | 15450 | 15450 | 15450 | 15450 | 15450
Occupant Population - 888 | 20 | 24 | 48 | 124 | 89 | 133 | 99 | 101 | 90 | 132
CONTRACTOR FILL OUT
Operating CFM | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866
Confirm DCV Disabled (yes or no) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Confirm operating hours in the BAS | 5am - 5pm | 5am - 5pm | 5am - 5pm | 5am - 5pm | 5am - 5pm | 5am - 5pm | 5am - 5pm | 5am - 5pm | 5am - 5pm | 5am - 5pm
Measured Return CFM | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Measured Maximum OA CFM | 2000 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400 | 2400
Measured Minimum OA CFM | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317 | 317
OA Meas. Method (Direct PT or SA-RA PT)
>(If SA-RA) Measured Supply Air | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
>(If SA-RA) Measured Return Air | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Pre-filter MERV Rating (or N/A) | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13
Pre-filter size | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2 | 24x24x2 & 12x24x2
Final Filter MERV Rating | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13 | MERV13
Final Filter size | 24x24x4 & 12x24x4 | 24x24x4 & 12x24x4 | 24x24x4 & 12x24x4 | 24x24x4 & 12x24x4 | 24x24x2 & 12x24x2 | 24x24x4 & 12x24x4 | 24x24x4 & 12x24x4 | 24x24x4 & 12x24x4 | 24x24x4 & 12x24x4 | 24x24x4 & 12x24x4 | 24x24x4 & 12x24x4
Comments / Corrective actions