## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINNING | 5200 | 5117 | 4300 | 4271 | 900 | 846 | 17.31% | 16.53%
RTU-2 | KITCHEN | 5000 | 5320 | 4050 | 4359 | 950 | 961 | 19% | 18.06%
RTU-OA | ROOF | 3250 | 3542 | 1250 | 1422 | 2000 | 2120 | 61.54% | 59.85%
PRV 2 | KITCHEN | [10 empty] | 1500 | 1475
PRV 3 | KITCHEN | [10 empty] | 1500 | 1513
PRV 4 | KITCHEN | [10 empty] | 350 | 384
EF-1 | RESTROOM | [12 empty] | 220 | 210
EF-2 | MOP ROOM | [12 empty] | 50 | 45
EF-3 | RESTROOM | [12 empty] | 70 | 74
TOTALS |  | 13450 | 13979 | 9600 | 10052 | 3850 | 3927 |  |  | 0 | 0 | 3350 | 3372 | 340 | 329
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3850 | 3927 |  | FRONT |  | 0.0109 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3701 |  | SIDE |  | 0.0127 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 160 | 226 |  | REAR |  | 0.0039 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0091667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0