## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 3014 | 2200 | 2189 | 800 | 825 | 26.67% | 27.37%
RTU-2 | KITCHEN | 3000 | 3174 | 2200 | 2368 | 800 | 806 | 26.67% | 25.39%
EF-1 | HOOD 1 | [10 empty] | 1000 | 1001
EF-2 | RESTROOM | [12 empty] | 300 | 303
TOTALS |  | 6000 | 6188 | 4400 | 4557 | 1600 | 1631 |  |  | 0 | 0 | 1000 | 1001 | 300 | 303
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1600 | 1631 |  | FRONT |  | 0.0072 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1300 | 1304 |  | SIDE |  | 0.0034 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 300 | 327 |  | REAR |  | 0.0088 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0064667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0