## Sheet1
Equipment | Pages in Report | Location | Issue | Maintenance | Remodel | Notes
EF-13 | 7, 46 | Meat/Seafood Hood | Lid covering the motor & pulleys is missing. Pulleys rusted and seized as result.
EF-8 | 9, 41 | Right Kitchen Hood | Grease trap missing.
EF-8 | 9, 41 | Right Kitchen Hood | No hinge kit installed.
EF-A8 | 10, 49 | Left Kitchen Hood | Grease trap missing.
EF-A8 | 10, 49 | Left Kitchen Hood | No hinge kit installed.
SF-1 | 11, 50 | Right Kitchen Hood | Intake filters damaged.
SF-2 | 11, 51 | Left Kitchen Hood | Intake filters not installed.
All RTUs | 5, 31-40 | Throughout Space | The return grilles are dirty throughout the space.
EF-11 | 6, 44 | Elevator Mech. Room | Fan has power, but is not functional.
EF-16 | 8, 48 | Dock Area Mezzanine | Fan has power, but is not functional.
RTU-3 | 12, 34 | Rear Dock | No outside air intake.
RTU-4 | 12, 35 | Bakery | No outside air intake.
RTU-5 | 12, 36 | Mezzanine / Offices | No outside air intake.
RTU-9 | 12, 40 | Dock Area Offices | No outside air intake.
RTU-6 | 13, 37 | Customer Service | Unit is not functional.
RTU-7 | 14, 38 | Mezzanine Conf & Break Room | Within RTU-7 the VFD is missing the cover/face of the drive.
RTU-9 | 15, 40 | Dock Area Offices | Ductwork transitions into a duct constructed out of plywood.
RTU-9 | 16, 40 | Dock Area Offices | Unit is not functional.
SF-2 | 17, 51 | Left Kitchen Hood | Unit is not functional.