## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
WSHP-1 | KITCHEN | 800 | 1144 | 665 | 1027 | 135 | 117 | 16.88% | 10.23%
WSHP-2 | DINING | 1400 | 955 | 1095 | 659 | 305 | 296 | 21.79% | 30.99%
WSHP-3 | BOH | 1200 | 0 | 1200 | 0 | 0 | 0 | 0% | #DIV/0!
MAU-1 | KITCHEN HD | [8 empty] | 2000 | 2194
KEF-1 | KITCHEN HD | [10 empty] | 2175 | 2132
EF-1 | RESTROOM | [12 empty] | 70 | 75
TOTALS |  | 3400 | 2099 | 2960 | 1686 | 440 | 413 |  |  | 2000 | 2194 | 2175 | 2132 | 70 | 75
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2440 | 2607 |  | FRONT |  | -0.04 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2245 | 2207 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 195 | 400 |  | REAR |  | 0.0053 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.01735 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Rear door connected to rest of building. It appears PopUp Bagels is positively pressurized but the entire building is averaging negative.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0