## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 4000 | 4220 | 3500 | 3688 | 500 | 532 | 12.5% | 12.61%
RTU-2 | DINING | 4000 | 3896 | 3000 | 2893 | 1000 | 1003 | 25% | 25.74%
MUA-1 | KITCHEN HOOD | [8 empty] | 565 | 526
EF-1 | KITCHEN HOOD | [10 empty] | 1800 | 1808
EF-2 | RESTROOM | [12 empty] | 150 | 154
TOTALS |  | 8000 | 8116 | 6500 | 6581 | 1500 | 1535 |  |  | 565 | 526 | 1800 | 1808 | 150 | 154
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2065 | 2061 |  | FRONT |  | 0.0187 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1950 | 1962 |  | SIDE |  | 0.0097 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 115 | 99 |  | REAR |  | 0.0126 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.013667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250