## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3500 | 3543 | 3000 | 3030 | 500 | 513 | 14.29% | 14.48%
RTU-2 | DINING | 4350 | 0 | 3350 | 0 | 1000 | 0 | 22.99% | #DIV/0!
MUA-1 | KITCHEN HD | [8 empty] | 1300 | 1391
EF-1 | KITCHEN HD | [10 empty] | 2550 | 2493
EF-2 | RESTROOM | [12 empty] | 150 | 156
TOTALS |  | 7850 | 3543 | 6350 | 3030 | 1500 | 513 |  |  | 1300 | 1391 | 2550 | 2493 | 150 | 156
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2800 | 1904 |  | FRONT |  | -0.023 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2700 | 2649 |  | SIDE |  | -0.057 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | -745 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | -0.04 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
BS as of 10/29/25 with RTU-2 inoperable
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0