## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 4000 | 2725 | 3000 | 2725 | 1000 | 0 | 25% | 0%
RTU-2 |  | 2600 | 2621 | 2100 | 2621 | 500 | 0 | 19.23% | 0%
RTU-3 |  | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0!
MUA-1 | [9 empty] | 2250 | 1980
KEF-1 | [11 empty] | 3600 | 4317
KEF-2 | [11 empty] | 0 | 0
EF-3 | [11 empty] | 150 | 0
TOTALS |  | 6600 | 5346 | 5100 | 5346 | 1500 | 0 |  |  | 2250 | 1980 | 3750 | 4317 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3750 | 1980 |  | FRONT |  | -0.068 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3750 | 4317 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | -2337 |  | REAR | [10 empty] | FALSE
[5 empty] | AVERAGE |  | -0.068 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0