## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | DINING A | 2500 | 2705 | 1925 | 2109 | 575 | 596 | 23% | 22.03%
AC-2 | KITCHEN | 9500 | 9226 | 7400 | 7135 | 2100 | 2091 | 22.11% | 22.66%
AC-3 | DINING B | 4920 | 4127 | 3820 | 3131 | 1100 | 996 | 22.36% | 24.13%
AC-4 | PLAY AREA | 2000 | 1524 | 1700 | 1524 | 300 | 0 | 15% | 0%
AC-5 | BOH | 1200 | 1214 | 1000 | 1006 | 200 | 208 | 16.67% | 17.13%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1554
EF-2 | HOOD 2 | [10 empty] | 701 | 675
EF-3 | RESTROOMS | [12 empty] | 530 | 479
EF-4 | HOOD 3 | [10 empty] | 390 | 393
TOTALS |  | 20120 | 18796 | 15845 | 14905 | 4275 | 3891 |  |  | 0 | 0 | 3003 | 2622 | 530 | 479
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4275 | 3891 |  | FRONT |  | 0.31 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3533 | 3101 |  | SIDE |  | 0.3 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 742 | 790 |  | REAR |  | 0.3 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.30333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390