## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2975 | 2776 | 0 | 0 | 2975 | 2776 | 100% | 100%
FC-1 | REMOTE BOH | 1400 | 1315 | 1400 | 1315 | 0 | 0 | 0% | 0%
FC-3 | DINING | 1500 | 1567 | 1500 | 1567 | 0 | 0 | 0% | 0%
KEF-1 | HOODS | [10 empty] | 2475 | 2477
EF-1 | RESTROOM | [12 empty] | 100 | 108
EF-2 | RESTROOMS | [12 empty] | 100 | 99
TOTALS |  | 5875 | 5658 | 2900 | 2882 | 2975 | 2776 |  |  | 0 | 0 | 2475 | 2477 | 200 | 207
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2975 | 2776 |  | FRONT |  | 0.02 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2675 | 2684 |  | SIDE |  | 0.018 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 300 | 92 |  | REAR |  | 0.019 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.019 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2975 | 2776
TOTAL KITCHEN EXHAUST |  | 2475 | 2477
NET AIRFLOW |  | 500 | 299
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0