## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS 1 | SALES | 3200 | 3260 | 0 | 0 | 3200 | 3260 | 100% | 100%
RTU-1 | OFFICE | 1750 | 1830 | 1610 | 0 | 140 | 137 | 0% | 7.486%
RTU-2 | STOCKROOM` | 1750 | 2077 | 1750 | 2077 | 0 | 0 | 0% | 0%
RTU-3 | SALES | 1400 | 1744 | 1400 | 1744 | 0 | 0 | 0% | 0%
RTU-4 | SALES | 1350 | 1492 | 1350 | 1492 | 0 | 0 | 0% | 0%
RTU-5 | SALES | 4850 | 4847 | 4850 | 4847 | 0 | 0 | 0% | 0%
RTU-6 | SALES | 3850 | 3844 | 3850 | 3844 | 0 | 0 | 0% | 0%
EF-1 | RESTROOMS | [12 empty] | 325 | 220
EF-2 | IT CLOSET | [12 empty] | 1000 | 987
EF-3 | FITTING ROOM | [12 empty] | 640 | 509
TOTALS |  | 14950 | 19094 | 14810 | 14004 | 3340 | 3397 |  |  | 0 | 0 | 0 | 0 | 1965 | 1716
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3340 | 3397 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 1965 | 1716 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 1375 | 1681 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0