16 Lot summary 									07/03/2023

Upon arrival all doors to mall and outside are closed. Space pressure relative to outside is -0.039”. Space pressure relative to the mall is -0.035. The mall space pressure relative to outside is +0.0015.

Start of day BP -0.032, -0.039 direct reading across door to outside.

Hood readings were measured to validate exhaust air flow from (3) kitchen hoods.

Hood front left

121" hood with 6 filters 16x20

avg ft/min 224*12.48=2795

Hood front right

121" hood with 6 filters 16x20

avg ft/min 159*12.48=1984

Solo Hood Back

157" hood with (7) 16x20 filters, (1) 16x16

avg ft/min 166*16.18=2685

Total Hood CFM = 7,464cfm

Actions taken:

Adjusted OA on rtu-3 closer to 20%, 1256cfm.

Final building pressure measured at -0.03”

Charbroiler

Initial single temp at thermometer- 9am- 213deg (dining room open to outside)

final single temp thermometer- 4pm- 223 deg (dining still open to outside)

Laser thermal spotting shows temps from 300-500 deg, see video (dining still open to outside)

Pass through window observing velocities from 77-96fpm when spanning from left to right with dining doors open. Velocities observed to fluctuate with 70-82fpm with dining doors closed. Temperatures above were obtained with dining room doors open.

Based upon the temperature readings directly above the Charbroiler, the velocity thru the pass-through window, the data showed no affect on temperature variance on the piece of equipment. The negative pressure only impacts the supply duct in dining area causing it to sweat & will be warmer than normal due to the warm air pulling into space with garage doors open.