## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | EXAM/DENTAL | 1200 | 1250 | 1095 | 1139 | 105 | 111 | 8.75% | 8.88%
RTU-2 | RECEPT/TRMNT | 3000 | 2576 | 2705 | 2275 | 295 | 301 | 9.833% | 11.68% | [5 empty] | 61
RTU-3 | EXAM/OFFICES | 1200 | 1232 | 980 | 1019 | 220 | 213 | 18.33% | 17.29% | [5 empty] | 51
EF-1 | EXAM RM | [12 empty] | 450 | 450
EF-2 | EXAM RM | [12 empty] | 275 | 281
TOTALS |  | 5400 | 5058 | 4780 | 4433 | 620 | 625 |  |  | 0 | 0 | 0 | 0 | 725 | 843
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 620 | 625 |  | FRONT |  | -0.0017 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 725 | 843 |  | SIDE |  | -0.0042 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -105 | -218 |  | REAR |  | -0.0011 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0023333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0