## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6000 | 5840 | 4050 | 3996 | 1950 | 1844 | 32.5% | 31.58%
RTU-2 | KITCHEN | 6000 |  | 4100 | 0 | 1900 |  | 31.67% | #DIV/0!
PRV-1 | RESTROOMS | [12 empty] | 375 | 373
PRV-2 | HD1 GRIDDLE | [10 empty] | 1500 | 1487
PRV-3 | HD2 FRYERS | [10 empty] | 1500 | 1522
PRV-4 | HD3 DISHWASHER | [10 empty] | 350
EF-1 | MOP ROOM | [12 empty] | 75 | 73
TOTALS |  | 12000 | 5840 | 8150 | 3996 | 3850 | 1844 |  |  | 0 | 0 | 3350 | 3009 | 450 | 446
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3850 | 1844 |  | FRONT | [10 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3800 | 3455 |  | SIDE |  | -0.0158 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | -1611 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0158 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0