## AHU-1
National TAB
Project: Crave - Westedge
Address: 99 WESTEDGE STE 1100 CHARLESTON, SC
Asset: AHU-1 (EXISTING) |  | Area: DINING AREA
Unit Data |  |  |  |  | Test Data
MFG | CARRIER |  |  |  |  | Design | Actual
Model Num | FB4CNP048 |  |  |  | SA CFM | 1600 | 1451
Serial Num | 2017A83728 |  |  |  | Fan Speed |  | DD / HIGH
[5 empty] | OA CFM | 375 | 75
[5 empty] | RA CFM | 1225 | 1376
Motor Data |  |  |  |  | RL Voltage | 208 | 211
Motor MFG | N/L |  |  |  | RL Amperage |  | 3.2
Horsepower | 0.75 |  |  |  | Suction ESP |  | -0.398
Motor Rpm | N/L |  |  |  | Discharge ESP |  | 0.127
Phase | 1 |  |  |  | Total ESP | 0.5 | 0.525
Voltage (rated) | 208 |  |  |  | Brake HP |  | N/A
Amperage (rated) | 3 |  |  |  | OUTSIDE AIR DUCT IS NOT DUCTED TO THE UNIT, UNIT HAS OPEN RETURN AND IS NOT ABLE TO PULL THE REQUIRED CFM THROUGH DUCTWORK. RECOMMEND A BOOSTER FAN BE INSTALLED/ ADDED
OA IN-LINE DAMPER IS 100% OPEN AND LOOVERS ARE OPEN AND DO NOT HAVE DAMPERS INSTALLED IN THEM.
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-1 | 100 | A | 12X12 | 400 | 363 | 360 | 0.9
1-2 | 100 | A | 12X12 | 400 | 347 | 364 | 0.91
1-3 | 100 | A | 12X12 | 400 | 386 | 366 | 0.915
1-4 | GAMING | A | 12X12 | 400 | 364 | 361 | 0.9025
|  |  |  | 1600 |  | 1451 | 0.90687
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## AHU-2
National TAB
Project: Crave - Westedge
Address: 99 WESTEDGE STE 1100 CHARLESTON, SC
Asset: AHU-2 (EXISTING) |  | Area: DINING AREA
Unit Data |  |  |  |  | Test Data
MFG | CARRIER |  |  |  |  | Design | Actual
Model Num | FB4CNPO48 |  |  |  | SA CFM | 1600 | 1450
Serial Num | 2017A83740 |  |  |  | Fan Speed |  | DD / HIGH
[5 empty] | OA CFM | 400 | 151
[5 empty] | RA CFM | 1200
Motor Data |  |  |  |  | RL Voltage | 208 | 211
Motor MFG | N/L |  |  |  | RL Amperage |  | 3.1
Horsepower | 0.75 |  |  |  | Suction ESP |  | -0.571
Motor Rpm | N/L |  |  |  | Discharge ESP |  | 0.105
Phase | 1 |  |  |  | Total ESP | 0.5 | 0.676
Voltage (rated) | 208 |  |  |  | Brake HP |  | N/A
Amperage (rated) | 6 |  |  |  | OUTSIDE AIR DUCT IS NOT DUCTED TO THE UNIT, UNIT HAS OPEN RETURN AND IS NOT ABLE TO PULL THE REQUIRED CFM THROUGH DUCTWORK. RECOMMEND A BOOSTER FAN BE INSTALLED/ ADDED. OA IN-LINE DAMPER IS 100% OPEN AND LOOVERS ARE OPEN AND DO NOT HAVE DAMPERS INSTALLED IN THEM.
SGRD5 DAMPER IS 100% OPEN UNIT IS RUNNING IN HIGH SPEED, GRILL IS UNABLE TO REACH DESIGN CFM. UNIT TOTAL IS WITHIN DESIGN.
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-1 | 100 | A | 12X12 | 300 | 272 | 290 | 0.96667
2-2 | 100 | A | 12X12 | 300 | 266 | 279 | 0.93
2-3 | 100 | A | 12X12 | 300 | 278 | 302 | 1.0067
2-4 | 100 | A | 12X12 | 350 | 407 | 325 | 0.92857
2-5 | GAMING | A | 12X12 | 350 | 223 | 254 | 0.72571
|  |  |  | 1600 |  | 1450 | 0.90625
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## AHU-3
National TAB
Project: Crave - Westedge
Address: 99 WESTEDGE STE 1100 CHARLESTON, SC
Asset: AHU-3 (EXISTING) |  | Area: DINING AREA
Unit Data |  |  |  |  | Test Data
MFG | CARRIER |  |  |  |  | Design | Actual
Model Num | FB4CNP048 |  |  |  | SA CFM | 1600 | 1456
Serial Num | 2017A83733 |  |  |  | Fan Speed |  | DD / HIGH
[5 empty] | OA CFM | 275 | 90
[5 empty] | RA CFM | 1325 | 1366
Motor Data |  |  |  |  | RL Voltage | 208 | 211
Motor MFG | N/L |  |  |  | RL Amperage |  | 3.3
Horsepower | 0.75 |  |  |  | Suction ESP |  | -0.679
Motor Rpm | N/L |  |  |  | Discharge ESP |  | 0.25''
Phase | 1 |  |  |  | Total ESP | 0.5 | 0.929
Voltage (rated) | 208 |  |  |  | Brake HP |  | N/A
Amperage (rated) | 6 |  |  |  | OUTSIDE AIR DUCT IS NOT DUCTED TO THE UNIT, UNIT HAS OPEN RETURN AND IS NOT ABLE TO PULL THE REQUIRED CFM THROUGH DUCTWORK. RECOMMEND A BOOSTER FAN BE INSTALLED/ ADDED
OA IN-LINE DAMPER IS 100% OPEN AND LOOVERS ARE OPEN AND DO NOT HAVE DAMPERS INSTALLED IN THEM.
SGRD7 DAMPER IS 100% OPEN UNIT IS RUNNING IN HIGH SPEED, GRILL IS UNABLE TO REACH DESIGN CFM. UNIT TOTAL IS WITHIN DESIGN.
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
3-1 | 106 | B | 24X24 | 250 | 281 | 236 | 0.944
3-2 | 108 | C | 9X9 | 75 | 88 | 72 | 0.96
3-3 | 107 | C | 9X9 | 75 | 55 | 68 | 0.90667
3-4 | 104 | B | 24X24 | 150 | 207 | 151 | 1.0067
3-5 | 108 | C | 9X9 | 50 | 49 | 55 | 1.1
3-6 | 100 | A | 12X12 | 300 | 273 | 293 | 0.97667
3-7 | 100 | A | 12X12 | 275 | 55 | 185 | 0.67273
3-8 | 100 | A | 12X12 | 425 | 375 | 396 | 0.93176
|  |  |  | 1600 |  | 1456 | 0.91
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## AHU-4
National TAB
Project: Crave - Westedge
Address: 99 WESTEDGE STE 1100 CHARLESTON, SC
Asset: AHU-3 (EXISTING) |  | Area: PRODUCTION AREA
Unit Data |  |  |  |  | Test Data
MFG | CARRIER |  |  |  |  | Design | Actual
Model Num | FB4CNP048 |  |  |  | SA CFM | 1600 | 1477
Serial Num | 2017A83755 |  |  |  | Fan Speed |  | DD / HIGH
[5 empty] | OA CFM | 175 | 65
[5 empty] | RA CFM | 1425 | 1412
Motor Data |  |  |  |  | RL Voltage | 208 | 211
Motor MFG | N/L |  |  |  | RL Amperage |  | 2.8
Horsepower | 0.75 |  |  |  | Suction ESP |  | -0.393
Motor Rpm | N/L |  |  |  | Discharge ESP |  | 0.16
Phase | 1 |  |  |  | Total ESP | 0.5 | 0.553
Voltage (rated) | 208 |  |  |  | Brake HP |  | N/A
Amperage (rated) | 6 |  |  |  | OUTSIDE AIR DUCT IS NOT DUCTED TO THE UNIT, UNIT HAS OPEN RETURN AND IS NOT ABLE TO PULL THE REQUIRED CFM THROUGH DUCTWORK. RECOMMEND A BOOSTER FAN BE INSTALLED/ ADDED
OA IN-LINE DAMPER IS 100% OPEN AND LOOVERS ARE OPEN AND DO NOT HAVE DAMPERS INSTALLED IN THEM.
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
4-1 | 102 | B | 12X12 | 200 | 167 | 181 | 0.905
4-2 | 102 | B | 12X12 | 200 | 185 | 190 | 0.95
4-3 | 102 | A | 12X12 | 200 | 196 | 182 | 0.91
4-4 | 102 | B | 12X12 | 200 | 184 | 185 | 0.925
4-5 | 100 | B | 12X12 | 400 | 365 | 379 | 0.9475
4-6 | 100 | B | 12X12 | 400 | 356 | 360 | 0.9
|  |  |  | 1600 |  | 1477 | 0.92312
Note on A5: USE FOR: FAN COIL UNIT SPLIT SYSTEM FURNACE HEAT PUMP

## EF-1
National TAB
Project: Crave - Westedge
Address: 99 WESTEDGE STE 1100 CHARLESTON, SC
Asset: EF-1 |  |  | Area: BUILDING EXHAUST
Unit Data |  |  |  |  | Test Data
MFG |  | LOREN COOK COMPANY |  |  |  | Design | Actual
Model Num |  | GEMINI 700 |  |  | CFM | 750 | 781
Serial Num |  | N/L |  |  | Fan RPM | 900 | DD / HIGH
Type |  | INLINE |  |  | RL Voltage | 115 | 121
[5 empty] | RL Amperage |  | 3.9
Motor Data |  |  |  |  | Suction ESP |  | -0.219
Motor MFG |  | LOREN COOK COM. |  |  | Total ESP | 0.5 | 0.219
Frame |  | N/L
Horsepower |  | 149W |  |  | EF1 - EGRD3 IS LOW OF DESIGNCFM DAMPER IS 100% OPEN. FAN TOTAL IS WITHIN DESIGN CFM. FAN IS RUNNING IN HIGH SPEED
Motor Rpm |  | N/L
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated) |  | 3.9
Service Factor |  | 1
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E1-1 | 108 | E | 10X10 | 125 | 142 | 119 | 0.952
E1-2 | 102 | E | 10X10 | 125 | 144 | 124 | 0.992
E1-3 | 102 | E | 10X10 | 300 | 244 | 250 | 0.83333
E1-4 | 107 | E | 10X10 | 125 | 141 | 128 | 1.024
E1-5 | 108 | E | 10X10 | 75 | 119 | 77 | 1.0267
|  |  |  | 750 |  | 698 | 0.93067
-