## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3416 | 2450 | 2425 | 950 | 991 | 27.94% | 29.01%
RTU-2 | DINING | 4000 | 4034 | 2850 | 2868 | 1150 | 1166 | 28.75% | 28.9%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1950
EF-1 | KITCHEN HOOD | [10 empty] | 3200 | 3224
EF-3 | KITCHEN HOOD | [10 empty] | 600 | 615
EF-2 | RESTROOM | [12 empty] | 150 | 157
TOTALS |  | 7400 | 7450 | 5300 | 5293 | 2100 | 2157 |  |  | 1950 | 1950 | 3800 | 3839 | 150 | 157
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4050 | 4107 |  | FRONT |  | 0.004 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3950 | 3996 |  | SIDE |  | 0.002 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 111 |  | REAR |  | 0.002 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0026667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD1 | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250
HD2 | CAPTIVE-AIRE | [11 empty] | 600