## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | DINING | 6000 | 5997 | 4050 | 4068 | 1950 | 1929 | 32.5% | 32.17%
RTU-2 | KITCHEN | 6000 | 6083 | 4050 | 4140 | 1950 | 1943 | 32.5% | 31.94%
PRV 2 | HD GRIDDLE | [10 empty] | 1500 | 1512
PRV 3 | HD FRYER | [10 empty] | 1500 | 1507
PRV 4 | DISH HOOD | [10 empty] | 350 | 367
EF 1 | MOP ROOM | [12 empty] | 75 | 52
PRV 1 | RESTROOM | [12 empty] | 375 | 377
TOTALS |  | 12000 | 12080 | 8100 | 8208 | 3900 | 3872 |  |  | 0 | 0 | 3350 | 3386 | 450 | 429
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3900 | 3872 |  | FRONT |  | 0.0038 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3815 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 57 |  | REAR |  | 0.0034 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0036 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0