## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 7833 | 7000 | 5981 | 1750 | 1852 | 20% | 23.64%
AC-2 | DINING A | 2890 | 2958 | 2290 | 2321 | 600 | 637 | 20.76% | 21.53%
AC-3 | DINING B NORTH | 4400 | 4391 | 3500 | 3486 | 900 | 905 | 20.45% | 20.61%
AC-4 | DINING B SOUTH | 2890 | 2433 | 2290 | 1805 | 600 | 628 | 20.76% | 25.81%
AC-5 | PLAYGROUND | 1800 | 1765 | 1500 | 1466 | 300 | 299 | 16.67% | 16.94%
AC-6 | MULTI-PURPOSE | 1100 | 1238 | 920 | 1051 | 180 | 187 | 16.36% | 15.11%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1805
EF-2 | HOOD 2 | [10 empty] | 701 | 645
EF-3 | HOOD 3 | [10 empty] | 701 | 700
EF-4 | RESTROOM | [12 empty] | 425 | 409
TOTALS |  | 21830 | 20618 | 17500 | 16110 | 4330 | 4508 |  |  | 0 | 0 | 3315 | 3150 | 425 | 409
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4330 | 4508 |  | FRONT |  | 0.017 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3740 | 3559 |  | SIDE |  | 0.015 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 590 | 949 |  | REAR |  | 0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.012 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390