## Survey
NOTE: WHILE LENNOX UNITS CAN BE ORDERED, UNITS CANNOT BE DELIVERED UNTIL 1ST QUARTER OF 2023
TAB Partner - |  |  |  |  | National TAB |  |  |  | Tech- |  |  |  | IAN FULLER | [11 empty] | CONDITION SURVEY | [15 empty] | Survey Due Date -
UNIT # |  |  |  | UNIT NAME | [5 empty] | STREET ADDRESS | [11 empty] | CITY | [8 empty] | ST |  | OPERATOR | [7 empty] | PHONE # | [8 empty] | EMAIL
1203 |  |  |  | EAGLE HARBOR FSU | [5 empty] | 1541 COUNTY RD 220 | [11 empty] | FLEMING ISLAND | [8 empty] | FL |  | CARY ARNOLD | [7 empty] | (904) 264-3644
CONSTRUCTION MGR (CM) | [5 empty] | SR PROGRAM MGR (SRP) | [5 empty] | SR PROGRAM LEAD (SRPL) | [7 empty] | FEQ FIELD CONSULTANT | [7 empty] | PROTO-TYPE |  |  |  |  | OPEN DATE |  |  |  | UNIT AGE |  |  | CONSTR START | [6 empty] | SCOPE OF WORK |  |  |  |  | ARCHITECT
AC# |  |  | SERIAL # |  |  |  | MODEL # | [6 empty] | TON |  |  | MFG. |  |  |  | AGE |  |  | HVAC UNIT TYPE/HUMIDITROL | [7 empty] | AREA SERVED |  |  |  |  | HEAT EXCH. |  |  | COND.DAM. |  |  |  | HAIL GARD |  |  |  |  | EVAP COIL |  | POW EXH | TOTAL
AC1 |  |  | 5619A05188 |  |  |  | LCH120H4MJ3Y | [6 empty] | 10 |  |  | Lennox | [6 empty] | ENERGENCE/ |  |  |  |  | 0 |  |  | KITCHEN |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 | 0
AC2 |  |  | 5613F00930 |  |  |  | LCH150S4BN3Y | [6 empty] | 12.5 |  |  | Lennox | [11 empty] | 0 |  |  | KITCHEN |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 537 | 537
AC3 |  |  | 5619G05973 |  |  |  | LCH102H4BG3Y | [6 empty] | 8.5 |  |  | Lennox | [11 empty] | 0 |  |  | DINING |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 | 0
AC4 |  |  | 5614F06782 |  |  |  | LCH092H4BN2Y | [6 empty] | 7.5 |  |  | Lennox | [11 empty] | 0 |  |  | DINING |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 | 0 | `
AC5 |  |  | 5616G09833 |  |  |  | LCH060H4EE3Y | [6 empty] | 5 |  |  | Lennox | [6 empty] | ENERGENCE/ | [7 empty] | PLAYROOM |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 | 0
AC6 | [36 empty] | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 | 0
AC7 | [36 empty] | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 0 | 0
AC8 | [31 empty] | TOTAL |  |  |  |  | 0 |  |  | 0 |  |  |  | 0 |  |  |  |  | 0 |  | 537 | 537
CRITICAL - Unable to Perform T & B Scope until Corrected by Responsible Party.
REVIEW & RECTIFY - If no action is taken T&B can be performed, but system performance will suffer.
NON-CRITICAL - Noted for consideration by project team, but not critical to system performance or fnctionality.
1. Using punch/screwdriver, prod heat exchanger tubes. If holes found and/or or prod test fail enter unit tonnage and lock out.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
2. Quantify damage/deterioration to the condenser coil (0% to 100%). If greater than 50% enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | 0% |  |  | AC2 |  |  | 0.1 |  | AC3 |  |  | 0% |  | AC4 |  | 10% |  |  | AC5 |  |  | 0% |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
3. Is there a hail guard installed on unit? If NO, enter unit tonnage. NOTE: If "CRITICAL", unit in top ten hail states.
|  | NON-CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
4. Check both sides of evaporator coil for deterioration. Perform fin test. If greater than 50% enter unit tonnage
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
5. Check for power exhaust at AC units greater than ten tons. If no power exhaust enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | 12.5 |  | AC3 |  |  | N/A |  | AC4 |  | N/A |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
6. Are there curb adaptors on any of the units? If YES, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | 7.5 |  |  | AC5 |  |  | 5 |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
7. See identified Humiditrol units below (HUM = HUMIDITROL).
|  | NON CRITICAL | [6 empty] | AC1 |  |  | HUM |  |  | AC2 |  |  | N/A |  | AC3 |  |  | HUM |  | AC4 |  | N/A |  |  | AC5 |  |  | NO |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
8. Is the humidity sensor wired? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | N/A |  | AC3 |  |  | C |  | AC4 |  | N/A |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
9. In table below record As-Built size of gas lines at gas meter riser, B1, B2, B3, B4, B5 etc. The cells below will auto populate when table is filled in.
|  | CRITICAL | [6 empty] | B1 |  |  | N/A |  |  | B2 |  |  | N/A |  | B3 |  |  | N/A |  | B4 |  | N/A |  |  | B5 |  |  | N/A |  | B6 |  |  |  | B7 | [5 empty] | B8
10. In the table below record the As-Built gas line drops D1, D2, D3, D4, D5 etc. The cells below will auto-populate when table in filled in.
|  | CRITICAL | [5 empty] | N/A | D1 |  |  | N/A |  |  | D2 |  |  | N/A |  | D3 |  |  | N/A |  | D4 |  | N/A |  |  | D5 |  |  | N/A |  | D6 |  | 0 |  | D7 |  |  | 0 |  |  | D8
ITEM 1 THROUGH 9 MISC. NOTES
UNITS ARE ELECTRIC, NO GAS PIPES
11. Record size of gas line going into unit. NOTE: Pull down menu in cells.
|  | CRITICAL | [6 empty] | AC1 | [5 empty] | AC2 |  |  |  |  | AC3 |  |  |  |  | AC4 |  |  |  |  | AC5 |  |  |  |  | AC6 |  |  |  | AC7 | [5 empty] | AC8
12. Is a smoke detector present in unit? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
13. Is the smoke detector inlet sampling tube capped? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | 10 |  |  | AC2 |  |  | 12.5 |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
14. Check smoke detector module light. If light RED or an AMBER color, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
15. Is smoke detector dust plugs capped? If YES, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | 8.5 |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
16. Is hub (hub houses bearings and located at center of pulley) at the tensioner intact? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A |  | AC3 |  |  | C |  | AC4 |  | N/A |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
17. Is belt tensioner installed? If NO, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
ITEM 9 THROUGH 16 MISC. NOTES
PIECE OF TAPE COVERING SAMPLE TUBE ON AC#2 HAS COME OFF
ELECTRIC UNITS NO GAS PIPES
18. Look for damage/indentions at pulleys? If damage found, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
20. Check motor sheave to assure it can be adjusted. If cannot be adJusted, enter unit tonnage, & part #'S in misc notes.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
21. Record belt size.
|  | N/A | [6 empty] | AC1 |  |  | AX54 |  |  | AC2 |  |  | A58 |  | AC3 |  |  | BX68 |  | AC4 |  | A59 |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
22. Identify any damage to the blower. If DAMAGE found, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
23. Quantify cleanliness of blower. If dirty, enter unit tonnage.
|  | NON CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | 12.5 |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | 5 |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
24. At blower motor start up is there a concernng amount of noise or vibration? If so, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
25. Is blank plate secured on B-cabinets? If NO, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
26. Is ductwork lined? If YES, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
ITEM 17 THROUGH 23 MISC. NOTES
27. Are turning vanes present in the supply ducts of the units? IF NO, insert unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
28. Are turning vanes single or double thickness? If DOUBLE, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
29. Is duct work seated and aligned? If NO, enter unit tonnage.
|  | N/A | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
30. Is canvas connector present? If NO, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | 10 |  |  | AC2 |  |  | 12.5 |  | AC3 |  |  | 8.5 |  | AC4 |  | 7.5 |  |  | AC5 |  |  | 5 |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
31. Quantify cleanliness of duct. If dirty, enter unit tonnage.
|  | NON CRITICAL | [6 empty] | AC1 |  |  | 10 |  |  | AC2 |  |  | 12.5 |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
32. If turning vanes not present, is drop radiused? If so, does radius equal the width of the duct? If not, enter tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N/A |  |  | AC2 |  |  | N/A |  | AC3 |  |  | N/A |  | AC4 |  | N/A |  |  | AC5 |  |  | N/A |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
33. Do units have prodigy boards? If no, enter unit tonnage (identify only if the AC unit is an Energence unit).
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
34. Identify prodigy boards New or Old. Answer New Green, N or Old Red, R.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | N |  |  | AC2 |  |  | R |  | AC3 |  |  | N |  | AC4 |  | N |  |  | AC5 |  |  | N |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
35. If economizer actuator open, turn unit off to assure it closes. If does not CLOSE enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
36. Are actuator gears worn? If yes, enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
37. Verify outdoor damper position can be adjusted. If cannot be adjusted enter unit tonnage.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
38. Is there any play in the actuator gear box? If yes, enter unit tonnage
|  | CRITICAL | [6 empty] | AC1 |  |  | 10.5 |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
39. Check economizer setting at prodigy board. If economizer set to zero, enter unit tonnage and re-set prodigy board to twenty percent.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
40. Do filters meet CFA spec (2" pleated polyester/cotton with MERV rating of 7). If no, enter unit tonnage.
|  | NON CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
ITEM 31 THROUGH 35 MISC. NOTES
41. Provide condensation pipe size. Minimum 1" at playland unit, and 1.25" at all other units. NOTE: DROP DOWN MENUS FOR PIPE SIZE.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | 1 |  |  | AC2 |  |  | 1 |  | AC3 |  |  | 1 |  | AC4 |  | 1 |  |  | AC5 |  |  | 1 |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
42. Do condensation traps meet provided detail. If NO, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | 10 |  |  | AC2 |  |  | 12.5 |  | AC3 |  |  | 8.5 |  | AC4 |  | 7.5 |  |  | AC5 |  |  | 5 |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
43. Do pre-filters need to be cleaned? If YES, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | 12.5 |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
44. Do pre-filters need to be replaced? If YES, enter unit tonnage.
|  | REVIEW & RECTIFY | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
45. Check Sun Coast panel terminal block for SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE. If single pair twisted with foil shield NOT present enter unit tonnage. See photo in insert twelve below.
|  | CRITICAL | [6 empty] | AC1 |  |  | C |  |  | AC2 |  |  | C |  | AC3 |  |  | C |  | AC4 |  | C |  |  | AC5 |  |  | C |  | AC6 |  | N/A |  | AC7 |  |  | N/A |  |  | AC8 |  |  | N/A
ITEM 36 THROUGH 39 MISC. NOTES
CONDENSATE DRAINS ARE NOT PVC
46. Is bathroom exhaust fan running? Enter YES or NO. | [23 empty] | NO.
47. Is bathroom exhaust fan making excessive noise? Enter Yes or NO. | [28 empty] | NO
48. Is bathroom exhaust fan vibrating excessively? Enter YES or NO. | [27 empty] | NO
49. Does bathroom exhaust fan have a back draft damper? Enter YES or NO. | [31 empty] | YES
50. Does bathroom exhaust fan duct have a liner? Enter YES OR NO. | [26 empty] | YES
51. Visually inspect ductwork at bathroom exhaust fan, and rate cleanliness. Enter CLEAN OR DIRTY. | [40 empty] | DIRTY
52. Record model and serial number of Suncoast Panel. | [21 empty] | Model # |  |  |  | NOT FOUND | [10 empty] | Serial # |  |  |  | NOT FOUND
53. Is there a HES control panel visible? | [15 empty] | Yes |  |  | X |  |  | No
54. Are thermostats Robert Shaw (Gray Display) or Network (Blue Display) ? Enter "RS", "NW" for Robert Shaw and Network respectively. If thermostat not Robert Shaw or Network, enter NO. | [25 empty] | AC1 - |  | RS |  |  | AC2 - |  |  | RS |  | AC3 - |  | NW |  | AC4 - |  |  | RS |  |  | AC5 - |  |  | RS
[26 empty] | AC6 - |  |  |  |  | AC7 - |  |  |  |  | AC8 -
MISCELLANEOUS NOTES
LONGEST RUN ______ ' - 2018 INTERNATIONAL FUEL GAS CODE - BRANCH LENGTH METHOD - TOTAL BTU'S _________
|  | BRANCH PIPING (B#) | [19 empty] | DROP PIPING (D#)
|  | DESCRIPTION |  |  |  | BRANCH LENGTH/SIZE | [15 empty] | DESCRIPTION | [11 empty] | DROP LENGTH/SIZE | [16 empty] | PIPE SIZE | *OUTSIDE DIAMETER
|  | GAS LINE |  |  |  | LENGTH |  | AS-BUILT |  |  | DESIGN |  |  |  |  | CALC | [5 empty] | DROP |  |  | GAS LINE |  |  |  | DEVICE |  |  |  |  | LENGTH |  |  | AS-BUILT |  |  |  |  | DESIGN |  |  |  |  | CALC
[6 empty] | (ft) |  | (in) |  |  | (in) |  |  |  |  | (in) | [17 empty] | (ft) |  |  | (in) |  |  |  |  | (in) |  |  |  |  | (in) |  |  |  | 1/2" | 7/8"
|  | Meter to B1 |  |  |  | 7.7 | [15 empty] | D1 |  |  | B1 to |  |  |  | WH | [21 empty] | 3/4" | 1"
|  | B1 to B2 |  |  |  | 28 | [15 empty] | D2 |  |  | B2 to |  |  |  | RTU 2 | [21 empty] | 1" | 1-5/16"
|  | B2 to B3 |  |  |  | 18 | [15 empty] | D3 |  |  | B3 to |  |  |  | RTU 1 | [21 empty] | 1-1/4" | 1-5/8"
|  | B3 to B4 |  |  |  | 44 | [15 empty] | D4 |  |  | B4 to |  |  |  | RTU 3 | [21 empty] | 1-1/2" | 1-7/8"
[22 empty] | D5 |  |  | B4 to |  |  |  | RTU 4 | [21 empty] | 2" | 2-3/8"
[22 empty] | D6 |  |  | B6 to | [25 empty] | 2-1/2" | 2-7/8"
[22 empty] | D7 |  |  | B6 to | [25 empty] | 3' | 3-1/2"
[51 empty] | 3-1/2" | 4"
[51 empty] | 4" | 4-1/2"
*Approximate
ROOFTOP VIEW #1 | [23 empty] | ROOFTOP VIEW #2
INLET SAMPLING TUBE NOT CAPPED ON AC#1 & 2 | [23 empty] | DIRTY BLOWER ON AC#2 & 5
PRE-FILTERS ON AC#2 NEED TO BE CLEANED | [23 empty] | AC# 4 & 5 ON CURB ADAPTORS
DUST PLUG IN SMOKE ALARM IN AC#3 | [23 empty] | RESTROOM EF IS NOT WORKING
INSERT 12
NOTE TO TECHNICIAN:
1. TAKE TWO OVERALL PICTURES OF THE ROOF TOP AND THEN UPLOAD THOSE AS THE FIRST TWO PICTURES.
2. CHECK THAT AT THE SUNCOAST PANEL THAT "SINGLE PAIR TWISTED WITH FOIL SHIELD AND DRAIN WIRE" IS USED FOR EACH RTU. SEE EXAMPLE PICTURE BELOW:

## 2020 Chain
2020-10-01 |  | 0 | 2020-10-31
2020-11-01 |  | 0 | 2020-11-30
2020-12-01 |  | 0 | 2020-12-31
2021-01-01 |  | 0 | 2021-01-31
2021-02-01 |  | 0 | 2021-02-28
2021-03-01 |  | 0 | 2021-03-31
2021-04-01 |  | 0 | 2021-04-30
2021-05-01 |  | 0 | 2021-05-31
2021-06-01 |  | 0 | 2021-06-30
(2) Store No. | Survey Due Date | (3) Location Name | (4) SOW | (8) Construction Start Date (CSD) | (14) Prototype | (23) Region | TAB Partner | Street Address | City | State | (27) Operator | SR Program Lead (SRPL) | SR Development Manager (DM) | SR Construction Manager (CM) | SR Program Manager (SRP) | FEQ Field Consultant | (37) Architect | Open Date | Location Phone | Location E-mail | AC1 | [5 empty] | AC2 | [5 empty] | AC3 | [5 empty] | AC4 | [5 empty] | AC5 | [5 empty] | AC6 |  |  |  |  | AC7 |  |  |  |  | AC8
1 |  | Northeast | [18 empty] | Serial # | HUMIDITROL | Model # | Mfg Date | Age | Type | Serial # | HUMIDITROL | Model # | Mfg Date | Age | Type | Serial # | HUMIDITROL | Model # | Mfg Date | Age | Type | Serial # | HUMIDITROL | Model # | Mfg Date | Age | Type | Serial # | HUMIDITROL | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type | Serial # | Model # | Mfg Date | Age | Type
1877 | 2022-11-10 | Coral Springs FSU | MLv2/BI | 2023-07-08 | S03A | Southeast | National TAB | 1341 North University Drive | Coral Springs | FL | Samuel Poeana | Doug Wolfe |  | Mark Farol | Allison Doherty | Rusty Lewis | CPH | 03/15/2007 | (954) 753-0779 | 01877@chick-fil-a.com | 5619G03308 |  | LGH120H4BH3Y | 2019-07-01 | 3.6877 | ENER | 5619G01422 |  | LGH150H4BH1Y | 2019-07-01 | 3.6877 | ENER | 5619G01423 |  | LGH150H4BH1Y | 2020-04-05 | 2.9233 | ENER | 5605G12941 |  | LGA090H2BH3Y | 2005-07-01 | 17.6959 | L-SER | 5619G00830 |  | LGH060H4EH4Y | 2019-07-01 | 3.6877 | ENER
[51 empty] | 5614G02828 | LCH120H4BN3Y | 2014-07-01
Formulas:
Age = (TODAY()-[Mfg Date])/365

## Sheet1
DEVICE | GAS PIPE SIZE | CONDENSATION | DROP
PIPE SIZE
WH | 1/2" | 0.75 | D1
RTU 1 | 3/4" | 1 | D2
RTU 2 | 1" | 1.25 | D3
RTU 3 | 1-1/4" | 1.5 | D4
RTU 4 | 1-1/2" |  | D5
RTU 5 | 2" |  | D6
RTU 6 | 2-1/2" |  | D7
RTU 7 | 3" |  | D8
RTU 8 | 3-1/2" |  | D9
SLOC | 4"
DLOC
OMDC