## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 2000 | 1997 | 1680 | 1648 | 320 | 349 | 16% | 17.48%
RTU-2 | DINING | 1600 | 1608 | 1215 | 1227 | 385 | 381 | 24.06% | 23.69%
MUA-1 | COOKLINE | [8 empty] | 1630 | 1551
EF-1 | GRILL HD | [10 empty] | 1120 | 1105
EF-2 | OVEN HD | [10 empty] | 600 | 561
EF-3 | FRY HD | [10 empty] | 850 | 878
EF-4 | WOMENS RR | [12 empty] | 75 | 116
EF-5 | MENS RR | [12 empty] | 75 | 99
TOTALS |  | 3600 | 3605 | 2895 | 2875 | 705 | 730 |  |  | 1630 | 1551 | 2570 | 2544 | 150 | 215
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | TRUE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2335 | 2281 |  | FRONT |  | 0.001 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 2720 | 2759 |  | SIDE |  | NA |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | -385 | -478 |  | REAR |  | -0.027 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.013 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
RESTROOM EXHAUST FANS DO NOT HAVE ACCESSIBLE SPEED CONTROLS AND ARE OPERATING ABOVE DESIGN, CONTRIBUTING TO SLIGHTLY NEGATIVE PRESSURE IN THE BUILDING.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0